## Slide 1
Loxahatchee Deep Bed Filter Performance Evaluation

## Slide 2: Purpose of Today’s Meeting
Review data analysis/results from filter study
Discuss plan for developing full paper and conference abstracts
Discuss plan and needs for board-level version of this presentation

## Slide 3
Project History
The Loxahatchee filter upgrade provided an opportunity to evaluate different filter types and their effectiveness in removal of TSS, pathogens, and contaminants of emerging concern (CECs)

## Slide 4
Phase 1: Traveling Bed Filters (TBF) and Synthetic Media Filters (SMF)
CEC Sampling: Jan – Apr 2016
Project History
CEC Sampling: Mar 2018 – May 2019
Phase 2: Upgrade to Deep Bed Filters (DBF)
Timeline
The Loxahatchee filter upgrade provided an opportunity to evaluate different filter types and their effectiveness in removal of TSS, pathogens, and trace organic compounds (TOrCs)

## Slide 5: Project Objectives
Improve operational performance for creation of high quality reuse water
  Key parameters are TSS and turbidity
Analyze the impact of filter upgrade on TOrCs and pathogens
Analyze biodegradability and sorption to filter media and chlorine oxidation impacts removal of TOrCs

## Slide 6: Project Objectives
Improve filter performance for operational parameters like TSS and turbidity
Analyze the impact of filter upgrade on contaminants of concern (CECs) and pathogens
Analyze biodegradability and sorption to filter media and chlorine oxidation impacts removal of TOrCs
Poor Chlorine Oxidation | Good Chlorine Oxidation
Caffeine Carbamazepine Dilantin Fluoxetine Gemfibrozil Ibuprofen Meprobamate Sulfamethoxazole TCEP | Acetaminophen Triclosan
Key analytes categorized by chloramine oxidation
Chloramine Oxidation:
Destruction of parent molecule from reactions with chloramines

## Slide 7: Project Objectives
Improve filter performance for operational parameters like TSS and turbidity
Analyze the impact of filter upgrade on contaminants of concern (CECs) and pathogens
Analyze biodegradability and sorption to filter media and chlorine oxidation impacts removal of TOrCs
 | Poor Sorption | Good Sorption
Poor Biodegradation | Meprobamate Dilantin Sulfamethoxazole | TCEP Carbamazepine
Good Biodegradation | Gemfibrozil Ibuprofen | Acetaminophen Triclosan Caffeine Fluoxetine
Key analytes categorized by sorption and biodegradation
Biodegradation:
Destruction of parent compound by microbial action
Sorption:
Attachment of parent compound to active sites on solid substrate

## Slide 8: Impact on Operations: TSS and Turbidity Analysis

## Slide 9: Methods to Evaluate Operational Improvements: Two-Sample t Test
SMF + TBF
DBF
?
Mean TSS Removal for SMF + TBF
Mean TSS Removal for DBF (unknown)
Two-Sample t Test evaluates whether the difference between these means is statistically significant

## Slide 10: Upgrading to DBF Increased TSS Removal by Over 7.5%
Based on a Two Sample t-Test, estimated TSS removal is significantly different after DBF comes online
p-value (TSS): 4.4 x 10-198
where p-value < 0.05 is significant
SMF + TBF
DBF

## Slide 11: Average Effluent TSS Dropped Over 40% with DBF
SMF + TBF
DBF
Better
Worse

## Slide 12: Average Effluent Turbidity Dropped Nearly 25% with DBF
SMF + TBF
DBF
SMF + TBF
DBF

## Slide 13: Upgrading to DBF Significantly Reduced Effluent TSS and Turbidity
Based on a Two Sample t-Test, the mean TSS and turbidity are significantly different after DBF comes online
p-value (TSS): 4.5 x 10-212
p-value (turbidity): 2.8 x 10-78
where p-value < 0.05 is significant
SMF + TBF
DBF

## Slide 14: Trace Organic Contaminants (TOrCs) Analysis

## Slide 15: Methods to Evaluate TOrC and Pathogen Removal: Boxplots to Compare Filter Types and TOrC Attributes
Hypothetical data for SMF
No removal line

## Slide 16: Methods to Evaluate TOrC and Pathogen Removal: Boxplots to Compare Filter Types and TOrC Attributes
Hypothetical data for SMF
median
1st quartile
3rd quartile
interquartile range

## Slide 17: Methods to Evaluate TOrC and Pathogen Removal: Boxplots to Compare Filter Types and TOrC Attributes
Hypothetical data for SMF
median
1st quartile
3rd quartile
1.5 times interquartile range
No removal line
data > 1.5 interquartile range

## Slide 18: Methods to Evaluate TOrC and Pathogen Removal: Boxplots to Compare Filter Types and TOrC Attributes
Hypothetical data
 | Poor Sorption | Good Sorption
Poor Biodegradation | Meprobamate Dilantin Sulfamethoxazole | TCEP Carbamazepine
Good Biodegradation | Gemfibrozil Ibuprofen | Acetaminophen Triclosan Caffeine Fluoxetine
Good sorption and good biodegradation?
Poor sorption and poor biodegradation?
Key analytes categorized by sorption and biodegradation

## Slide 19: TOrCs Removal Near Zero across Filtration for All Filter Types
Full extent of removal data

## Slide 20: Based on Data Evaluation, Sorption Does Not Explain TOrC Removal
 | Poor Sorption | Good Sorption
 | Meprobamate Dilantin Sulfamethoxazole | TCEP Carbamazepine
 | Gemfibrozil Ibuprofen | Acetaminophen Triclosan Caffeine Fluoxetine

## Slide 21: Biodegradability Not Explanatory for Removal; Dynamic WW Flow and Concentration Impact Observed Removal
Poor Biodegradation | Meprobamate Dilantin Sulfamethoxazole | TCEP Carbamazepine
Good Biodegradation | Gemfibrozil Ibuprofen | Acetaminophen Triclosan Caffeine Fluoxetine

## Slide 22: Sorption and Biodegradability Not Explanatory for Removal
 | Poor Sorption | Good Sorption
Poor Biodegradation | Meprobamate Dilantin Sulfamethoxazole | TCEP Carbamazepine
Good Biodegradation | Gemfibrozil Ibuprofen | Acetaminophen Triclosan Caffeine Fluoxetine

## Slide 23: Chloramine Oxidation Category May Impact TOrC Removal
Poor Chlorine Oxidation | Good Chlorine Oxidation
Caffeine Carbamazepine Dilantin Fluoxetine Gemfibrozil Ibuprofen Meprobamate Sulfamethoxazole TCEP | Acetaminophen Triclosan

## Slide 24
Chloramine Oxidation Category May Impact TOrC Removal

## Slide 25: Triclosan Is Consistently Removed by Chloramine Oxidation
Poor Chlorine Oxidation | Good Chlorine Oxidation
Caffeine Carbamazepine Dilantin Fluoxetine Gemfibrozil Ibuprofen Meprobamate Sulfamethoxazole TCEP | Acetaminophen Triclosan
Within the “Good Chloramine Oxidation” category, Triclosan has the best removal performance.

## Slide 26: Pathogen Analysis

## Slide 27: Increased Removal of Pathogens Observed for DBF—Although Sample Sizes are Small
n = 7
n = 7
n = 6
n = 7
n = 7
n = 6

## Slide 28: Pathogen Reduction Correlates to Turbidity Breakthrough
Unpublished data from Ian Douglas, City of Ottawa, Filter Study on Surface Water Treatment
SMF + TBF
DBF

## Slide 29: Concluding Thoughts

## Slide 30: Project Objectives
Improve filter performance for operational parameters like TSS and turbidity
Filter upgrade to DBF:
Increased TSS removal by 7.5%
Decreased effluent TSS by 40%
Decreased effluent turbidity by 25%

## Slide 31: Project Objectives
Analyze the impact of filter upgrade on trace organic contaminants (TOrCs) and pathogens
Filter upgrade to DBF:
Had no observable impact on TOrC removal
Increased removal of Cryptosporidium and Giardia

## Slide 32: Project Objectives
Analyze biodegradability and sorption to filter media and chloramine impacts removal of TOrCs
Neither biodegradability nor sorption category has an impact on TOrC removal
However, chloramine oxidation category may have an impact on TOrC removal
Poor sorption,
Poor biodegradation
Good sorption,
Poor biodegradation
Poor sorption,
Good biodegradation
Good sorption,
Good biodegradation

## Slide 33: Additional Slides

## Slide 34: Upgrading to DBF Significantly Reduced TSS and Turbidity Based on Two-Sample t Test
SMF + TBF
DBF
Transition

## Slide 35: Upgrading to DBF Significantly Reduced TSS and Turbidity Based on Two-Sample t Test
SMF + TBF
DBF
Transition
SMF + TBF
DBF
Transition

## Slide 36: Upgrading to DBF Significantly Reduced TSS and Turbidity Based on Two-Sample t Test
Based on a Two Sample t-Test, the mean TSS and turbidity are significantly different after DBF comes online
p-value (TSS): 1.06 x 10-42
p-value (turbidity): 1.48 x 10-61
where p-value < 0.05 is significant
SMF + TBF
DBF
Transition

## Slide 37: Methodology and Assumptions
Non-detects are set to the minimum reporting level (MRL) of instrument.
Flow split assumption: based on SCADA data, calculations were made assuming an average of 1.71 MGD to traveling bed filters and 6.25 MGD to synthetic media filters.
For triplicate data, the mean value was used (analysis of variability shown below).

## Slide 38: DBF Shows Slight Increase in Average Turbidity Removal Compared to SMF and TBF
n = 29
n = 56
n = 15