## Weekly
Sample Location | TBF-I (FPS) | TBF-E (sand filters) | SMF-E (fuzzy filter #2) | Final (Chlorine Contact Effluent) | TBF-I (FPS) | TBF-E (sand filters) | SMF-E (fuzzy filter #2) | Final (Chlorine Contact Effluent) | TBF-I | TBF-E (sand filters) | SMF-E (fuzzy filter #2) | Final (Chlorine Contact Effluent) | TBF-I (FPS) | TBF-E (sand filters) | SMF-E (fuzzy filter #2) | Final (Chlorine Contact Effluent) | TBF-I (FPS) | TBF-E (sand filters) | SMF-E (fuzzy filter #2) | Final (Chlorine Contact Effluent) | TBF-I (FPS) | TBF-E (sand filters) | SMF-E (fuzzy filter #2) | Final (Chlorine Contact Effluent) | TBF-I (FPS) | TBF-E (sand filters) | SMF-E (fuzzy filter #2) | Final (Chlorine Contact Effluent) | TBF-I (FPS) | TBF-E (sand filters) | SMF-E (fuzzy filter #2) | Final (Chlorine Contact Effluent)
Sample Period | Week 1 | Week 1 | Week 1 | Week 1 | Week 2 | Week 2 | Week 2 | Week 2 | Week 3 | Week 3 | Week 3 | Week 3 | Week 4 | Week 4 | Week 4 | Week 4 | Week 5 | Week 5 | Week 5 | Week 5 | Week 6 | Week 6 | Week 6 | Week 6 | Week 7 | Week 7 | Week 7 | Week 7 | Week 8 | Week 8 | Week 8 | Week 8
Date Sampled | 2016-01-25 | 2016-01-25 | 2016-01-25 | 2016-01-25 | 2016-02-01 | 2016-02-01 | 2016-02-01 | 2016-02-01 | 2016-02-29 | 2016-02-29 | 2016-02-29 | 2016-02-29 | 2016-03-28 | 2016-03-28 | 2016-03-28 | 2016-03-28 | 2016-04-04 | 2016-04-04 | 2016-04-04 | 2016-04-04 | 2016-04-18 | 2016-04-18 | 2016-04-18 | 2016-04-18 | 2016-04-25 | 2016-04-25 | 2016-04-25 | 2016-04-25 | 2016-05-02 | 2016-05-02 | 2016-05-02 | 2016-05-02
Time Sampled | 9:35 | 9:28 | 9:50 | 9:15 | 9:45 | 9:30 | 8:58 | 9:15 | 9:47 | 9:37 | 9:20 | 10:12 | 9:05 | 9:11 | 10:25 | 9:20 | 9:55 | 9:50 | 9:35 | 10:05 | 9:45 | 9:50 | 9:30 | 9:55 | 9:25 | 9:40 | 9:45 | 9:55 | 9:20 | 9:15 | 9:00 | 9:30
No. of Crypto/Giardia Filters | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Filter #1 Lot # | FZ6107 | FZ6107 | FZ6107 | FZ6107 | FZ6107 | FZ6107 | FZ6107 | FZ6107 | FZ6107 | FZ6107 | FZ6107 | FZ6107 | FZ6107 | FZ6107 | FZ6107 | FZ6107 | FZ6107 | FZ6107 | FZ6107 | FZ6107 | FZ7962 | FZ7962 | FZ7962 | FZ7962 | FZ7962 | FZ7962 | FZ7962 | FZ7962 | FZ7962 | FZ7962 | FZ7962 | FZ7962
Filter #1 Serial # | 586243 | 586257 | 586245 | 586276 | 586253 | 586234 | 586241 | 586246 | 586491 | 586484 | 586493 | 586483 | 586464 | 586461 | 586460 | 586463 | 586431 | 586432 | 586430 | 586434 | 600132 | 600128 | 600130 | 600124 | 600237 | 600241 | 600242 | 600200 | 600204 | 600236 | 600230 | 600229
Filter #1 Time Start Filtration | 11:05 | 10:47 | 10:35 | 10:16 | 11:30 | 11:02 | 10:20 | 9:58 | 11:44 | 11:28 | 11:13 | 10:56 | 11:26 | 10:55 | 11:10 | 10:05 | 11:49 | 11:36 | 11:22 | 11:00 | 10:15 | 10:38 | 11:07 | 11:29 | 10:17 | 10:39 | 10:55 | 11:33 | 9:48 | 10:08 | 10:24 | 10:45
Filter #1 Time End Filtration | 11:20 | 11:01 | 10:45 | 10:29 | 11:46 | 11:24 | 10:56 | 10:15 | 11:51 | 11:37 | 11:20 | 11:03 | 11:31 | 11:03 | 11:15 | 10:10 | 11:59 | 11:44 | 11:30 | 11:10 | 10:28 | 11:00 | 11:24 | 11:50 | 10:25 | 10:45 | 11:03 | 11:39 | 9:57 | 10:17 | 10:30 | 10:51
Filter #1 Volume Filtered (L) | 5 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10.5 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10.5 | 10 | 10 | 10.5 | 10 | 10 | 10 | 10 | 10
Filter #2 Lot # | FZ6107
Filter #2 Serial # | 586243
Filter #2 Time Start Filtration | 11:21
Filter #2 Time End Filtration | 11:33
Filter #2 Volume Filtered (L) | 5
Total Volume Filtered (L) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10.5 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10.5 | 10 | 10 | 10.5 | 10 | 10 | 10 | 10 | 10
Meter Start (L/m) | 1 | 1 | 1 | 1 | 1 | 1 | 0.75 | 1 | 2 | 1.5 | 2 | 2 | 2 | 2 | 2 | 2 | 1.75 | 1.75 | 1.75 | 1.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1.75 | 2 | 2
Meter Stop (L/m) | 0.5 | 1 | 1 | 0.5 | 0.6 | 0.75 | 0.5 | 0.75 | 1.75 | 2 | 2 | 2 | 2 | 1.5 | 2 | 2 | 1 | 1.5 | 1.75 | 1.5 | 1 | 0.5 | 0.75 | 1 | 2 | 2 | 2 | 2 | 1.5 | 1.75 | 2 | 2
Sand Filter Flow (mgd) |  | 1.5 |  |  |  | 3 |  |  |  | 3 |  |  |  | 3 |  |  |  | 3 |  |  |  | 3 |  |  |  | 2 |  |  |  | 2.7
# sand filters online |  | 6 |  |  |  | 6 |  |  |  | 6 |  |  |  | 6 |  |  |  | 6 |  |  |  | 6 |  |  |  | 6 |  |  |  | 5
Sand Filter Loading Rate (gallons/ft2)
Fuzzy Filter Flow (mgd) |  |  | 4 |  |  |  | 7 |  |  |  | 6 |  |  |  | 6 |  |  |  | 6 |  |  |  | 6 |  |  |  | 4 |  |  |  | 5.2
# fuzzy filters online |  |  | 4 |  |  |  | 4 |  |  |  | 4 |  |  |  | 4 |  |  |  | 4 |  |  |  | 4 |  |  |  | 4 |  |  |  | 3
Fuzzy Filter Loading Rate (gallons/ft2)
Giardia Concentration (cysts/L) | 66 | 20 | 72 | 43 | 105 | 50 | 45 | 35 | 90 | 35 | 35 | 15 | 4 | 33 | 13 | < 0.3 | 200 | 25 | 40 | 25 | 40 | 130 | 60 | 19.048 | 115 | 15 | 42.857 | 25 | 95 | 10 | 25 | 15
Cryptosporidium Concentration (oocysts/L) | 26 | 13 | 27 | 26 | 40 | 30 | 15 | 10 | 25 | 15 | 35 | 15 | 1 | < 3 | 3 | < 0.3 | 30 | 5 | 15 | 5 | 10 | < 5 | 5 | < 4.762 | 25 | 20 | 14.286 | 10 | 10 | <5 | <5 | <5

## Daily Turbidity
Date | time axis 2016-01-25 to 2016-04-28
Time | 9:15 | 8:00 | 8:00 | 9:00 | 14:00 | 8:00 | 8:15 | 8:30 | 14:05 | 8:20 | 8:20 | 7:55 | 8:20 | 8:15 | 8:20 | 8:20 | 8:20 | 8:10 | 8:15 | 8:15 | 9:20 | 7:50 | 7:45 | 8:15 | 7:55 | 8:20 | 7:45 | 8:40 | 8:30 | 8:40 | 8:17 | 15:15 | 8:50 | 8:15 | 8:25 | 8:05 | 8:25 | 8:20 | 9:05 | 8:25 | 8:35 | 8:05 | 8:05 | 9:35 | 8:30 | 8:45 | 8:45 | 8:10 | 8:25 | 8:05 | 8:15 | 8:15 | 8:25 | 8:30 | 8:25 | 8:10 | 8:30 |  |  | 8:30 | 8:10 | 8:10
Turbidity (NTU) @ TBF-I (Filter Pump Station #1) | 6.2 | off-line | off-line | 6.8 | 7.7 | 9.3 | 6.6 | 8.1 | 4.7 | 7.5 | 5.6 | 5.1 | 5.4 | 6.7 | 7.1 | 7.7 | 7.5 | 6.8 | 9.2 | 8.5 | 5.2 | 6.9 | 10.9 | 15.3 | 8.5 | 16 | 6.2 | 4.3 | 6.4 | 29.1 | 24.6 | 7.8 | 10.1 | 7.4 | 5 | 9.4 | 6.6 | 10.6 | 3.3 | 5.9 | 6.3 | 8 | 5.1 | 13.1 | 7 | 6.1 | 5.5 | 9.6 | 7.8 | 6.8 | 11.7 | 6.7 | 6 | 7.2 | 6.3 | 6.7 | 16.1 |  |  | 5.6 | 4.6 | 5
Turbidity (NTU) @ TBF-E (sand filter effluent) | 5.3 | off-line | off-line | 4.1 | 5.3 | 5.2 | 3.6 | 5 | 4 | 15.6 | 7.9 | 3.9 | 4.5 | 6.7 | 6.1 | 7.8 | 6.6 | 9.1 | 5.2 | 6.2 | 4.8 | 4.2 | 3.3 | 2.6 | 3.8 | 3.3 | 3 | 3.9 | 3.3 | 10.1 | 25.4 | 4 | 3.6 | 3.4 | 5.4 | 5 | 3.8 | 5.2 | 10.4 | 5 | 4.4 | 3.3 | 3 | 4.2 | 4 | 4.3 | 3.4 | 6.2 | 5.1 | 4.8 | 4.2 | 4.5 | 5 | 5.8 | 6.7 | 3.8 | 6.6 |  |  | 4 | 4.4 | 3
Turbidity (NTU) @ SMF-E (fuzzy filter #1) | n/a | off-line | off-line | n/a | off-line | off-line | off-line | off-line | off-line | off-line | off-line | off-line | off-line | off-line | off-line | off-line | off-line | off-line | off-line | off-line | 3.4 | 4 | 2.3 | 2.8 | 4.1 | 2.3 | 2.5 | off-line | off-line | 2.6 | 3.1 | 2.8 | 2.9 | 2.5 | off-line | off-line | off-line | off-line | 2.8 | off-line | off-line | off-line | off-line | 4.4 | 3.4 | 3.5 | off-line | off-line | off-line | 2.9 | 3.2 | 16.8 | 2.4 | 3.2 | 3.8 | 4.5 | 4.6 |  |  | 3.1 | 2.7 | 2.5
Turbidity (NTU) @ SMF-E (fuzzy filter #2) | 4.5 | off-line | off-line | 4.7 | off-line | off-line | off-line | off-line | off-line | off-line | off-line | off-line | off-line | off-line | off-line | off-line | off-line | off-line | off-line | off-line | 3.7 | 4.5 | 4.1 | 3.7 | 4.4 | 4 | 3.4 | off-line | off-line | 6.3 | 3.7 | 3.2 | 3.7 | 3.6 | off-line | off-line | off-line | off-line | 3.2 | off-line | off-line | off-line | off-line | 4.4 | 3.4 | 4.2 | off-line | off-line | off-line | 3.4 | 3.9 | 4.3 | 3.2 | 4 | 3.9 | 4.6 | 5.7 |  |  | 3.6 | 2.9 | 2.6
Turbidity (NTU) @ SMF-E (fuzzy filter #3) | n/a | off-line | off-line | n/a | off-line | off-line | off-line | off-line | off-line | off-line | off-line | off-line | off-line | off-line | off-line | off-line | off-line | off-line | off-line | off-line | 3 | 4.1 | 2.7 | washing | 4.3 | 2.8 | 3 | off-line | off-line | 5.9 | 3.7 | 3.3 | 3.1 | 3 | off-line | off-line | off-line | off-line | 2.9 | off-line | off-line | off-line | off-line | 3.9 | 2.7 | 3 | off-line | off-line | off-line | 3.2 | 3.7 | 4.3 | 3.3 | 3.1 | 3.8 | 4.9 | 4.5 |  |  | off-line | 3.2 | 2.7
Turbidity (NTU) @ SMF-E (fuzzy filter #4) | n/a | off-line | off-line | n/a | off-line | off-line | off-line | off-line | off-line | off-line | off-line | off-line | off-line | off-line | off-line | off-line | off-line | off-line | off-line | off-line | 3.1 | 3.9 | 2.3 | 2.6 | washing | 2.1 | 2.2 | off-line | off-line | 3.3 | 3.1 | 2.6 | 2.7 | 2.1 | off-line | off-line | off-line | off-line | 2.5 | off-line | off-line | off-line | off-line | 3.9 | 2.3 | 2.8 | off-line | off-line | off-line | 2.9 | 3.2 | 4 | 2.9 | 2.8 | off-line | 2.7 | off-line |  |  | 2.6 | 2.1 | off-line
Turbidity (NTU) @ Final (Chlorine Contact Effluent) | 3.5 | off-line | off-line | 4.3 | 4.9 | 5.7 | 3.6 | 4.7 | 3.4 | 5.3 | 3.5 | 3.2 | 4.1 | 3.7 | 5.7 | 3.8 | 3.9 | 4 | 4.4 | 4.9 | 3.4 | 4.2 | 3.1 | 2.3 | 3.4 | 2.6 | 3.1 | 2.5 | 2.9 | 4.3 | 3.4 | 2.9 | 3.4 | 2.8 | 3.6 | 4 | 3.5 | 5 | 3.2 | 3.6 | 3.6 | 3.1 | 2.8 | 4 | 2.7 | 3.7 | 3.2 | 7 | 4.4 | 4.1 | 4.2 | 4.6 | 2.7 | 3.4 | 3.9 | 3.4 | 4.7 |  |  | 3.3 | 2.9 | 2.2
Sand Filter Flow (mgd) | 2016-01-25: 1.5; 2016-02-01: 3; 2016-02-29: 3; 2016-04-04: 3; 2016-04-05: 3; 2016-04-06: 3; 2016-04-07: 3; 2016-04-08: 3; 2016-04-11: 3; 2016-04-12: 3; 2016-04-13: 3; 2016-04-14: 3; 2016-04-15: 3; 2016-04-18: 3; 2016-04-19: 3; 2016-04-20: 3; 2016-04-21: 3
# sand filters online | 2016-01-25: 4; 2016-02-01: 6; 2016-02-29: 6; 2016-04-04: 6; 2016-04-05: 6; 2016-04-06: 6; 2016-04-07: 6; 2016-04-08: 6; 2016-04-11: 6; 2016-04-12: 6; 2016-04-13: 6; 2016-04-14: 6; 2016-04-15: 6; 2016-04-18: 6; 2016-04-19: 6; 2016-04-20: 6; 2016-04-21: 6
Sand Filter Loading Rate (gallons/ft2)
Fuzzy Filter Flow (mgd) | 2016-01-25: 4; 2016-02-01: 7; 2016-02-29: 6; 2016-04-04: 6; 2016-04-05: 6; 2016-04-06: 6; 2016-04-07: 6; 2016-04-08: 6; 2016-04-11: 6; 2016-04-12: 6; 2016-04-13: 6; 2016-04-14: 6; 2016-04-15: 6; 2016-04-18: 6; 2016-04-19: 6; 2016-04-20: 6; 2016-04-21: 6
# fuzzy filters online | 2016-01-25: 4; 2016-02-01: 4; 2016-02-29: 4; 2016-04-04: 4; 2016-04-05: 4; 2016-04-06: 4; 2016-04-07: 4; 2016-04-08: 4; 2016-04-11: 4; 2016-04-12: 4; 2016-04-13: 4; 2016-04-14: 4; 2016-04-15: 4; 2016-04-18: 4; 2016-04-19: 4; 2016-04-20: 4; 2016-04-21: 4
Fuzzy Filter Loading Rate (gallons/ft2)
Average Fuzzy Filter Turbidity (NTU) | 2016-01-25: 4.5; 2016-02-01: 4.7; 2016-02-29: 3.3; 2016-03-02: 4.125; 2016-03-03: 2.85; 2016-03-04: 3.0333; 2016-03-07: 4.2667; 2016-03-08: 2.8; 2016-03-09: 2.775; 2016-03-14: 4.525; 2016-03-15: 3.4; 2016-03-16: 2.975; 2016-03-17: 3.1; 2016-03-18: 2.8; 2016-03-21: #DIV/0!; 2016-03-22: #DIV/0!; 2016-03-23: #DIV/0!; 2016-03-24: #DIV/0!; 2016-03-28: 2.85; 2016-03-29: #DIV/0!; 2016-03-30: #DIV/0!; 2016-03-31: #DIV/0!; 2016-04-01: #DIV/0!; 2016-04-04: 4.15; 2016-04-05: 2.95; 2016-04-06: 3.375
Fuzzy Filter #1 actual-mean (NTU) | 2016-02-29: 0.1; 2016-03-02: -0.125; 2016-03-03: -0.55; 2016-03-04: -0.23333; 2016-03-07: -0.16667; 2016-03-08: -0.5; 2016-03-09: -0.275; 2016-03-14: -1.925; 2016-03-15: -0.3; 2016-03-16: -0.175; 2016-03-17: -0.2; 2016-03-18: -0.3; 2016-03-21: #VALUE!; 2016-03-22: #VALUE!; 2016-03-23: #VALUE!; 2016-03-24: #VALUE!; 2016-03-28: -0.05; 2016-03-29: #VALUE!; 2016-03-30: #VALUE!; 2016-03-31: #VALUE!; 2016-04-01: #VALUE!; 2016-04-04: 0.25; 2016-04-05: 0.45; 2016-04-06: 0.125
Fuzzy Filter #2 actual-mean (NTU) | 2016-01-25: 0; 2016-02-01: 0; 2016-02-29: 0.4; 2016-03-02: 0.375; 2016-03-03: 1.25; 2016-03-04: 0.66667; 2016-03-07: 0.13333; 2016-03-08: 1.2; 2016-03-09: 0.625; 2016-03-14: 1.775; 2016-03-15: 0.3; 2016-03-16: 0.225; 2016-03-17: 0.6; 2016-03-18: 0.8; 2016-03-21: #VALUE!; 2016-03-22: #VALUE!; 2016-03-23: #VALUE!; 2016-03-24: #VALUE!; 2016-03-28: 0.35; 2016-03-29: #VALUE!; 2016-03-30: #VALUE!; 2016-03-31: #VALUE!; 2016-04-01: #VALUE!; 2016-04-04: 0.25; 2016-04-05: 0.45; 2016-04-06: 0.825
Fuzzy Filter #3 actual-mean (NTU) | 2016-02-29: -0.3; 2016-03-02: -0.025; 2016-03-03: -0.15; 2016-03-07: 0.033333; 2016-03-08: 0; 2016-03-09: 0.225; 2016-03-14: 1.375; 2016-03-15: 0.3; 2016-03-16: 0.325; 2016-03-17: 0; 2016-03-18: 0.2; 2016-03-21: #VALUE!; 2016-03-22: #VALUE!; 2016-03-23: #VALUE!; 2016-03-24: #VALUE!; 2016-03-28: 0.05; 2016-03-29: #VALUE!; 2016-03-30: #VALUE!; 2016-03-31: #VALUE!; 2016-04-01: #VALUE!; 2016-04-04: -0.25; 2016-04-05: -0.25; 2016-04-06: -0.375
Fuzzy Filter #4 actual-mean (NTU) | 2016-02-29: -0.2; 2016-03-02: -0.225; 2016-03-03: -0.55; 2016-03-04: -0.43333; 2016-03-08: -0.7; 2016-03-09: -0.575; 2016-03-14: -1.225; 2016-03-15: -0.3; 2016-03-16: -0.375; 2016-03-17: -0.4; 2016-03-18: -0.7; 2016-03-21: #VALUE!; 2016-03-22: #VALUE!; 2016-03-23: #VALUE!; 2016-03-24: #VALUE!; 2016-03-28: -0.35; 2016-03-29: #VALUE!; 2016-03-30: #VALUE!; 2016-03-31: #VALUE!; 2016-04-01: #VALUE!; 2016-04-04: -0.25; 2016-04-05: -0.65; 2016-04-06: -0.575
*Samples collected within 15 minutes of each other can be treated as if they were collected at the same time. | bar: 2016-01-25 to 2016-02-04